## Slide 1: Impact and Control of Invasive Mussels at Hydropower Plants
Sherri Pucherelli
Biologist, TSC, Denver, CO

## Slide 2: Mussel Impacts at Reclamation

## Slide 3: Impacts at Hydropower Plants
Increased maintenance and unplanned outages
  Mussel attachment
    Low velocity, 4.5 feet per second or less
    Intakes, gates, instrumentation, small diameter pipes
  Shell debris
    Strainers and screens

## Slide 4: Challenges
Quantifying the impacts at our hydropower plants
  Not easy to track all maintenance and costs
Preparing for potential infestations is difficult
  Many variables that are facility specific

## Slide 5: Case Study Project
Compiled case studies describing plant experiences with mussels
Purpose:
  Understand impacts at Reclamation plants
  Information for managers preparing or considering changes to existing approaches
Commitment to the DOI Safeguarding the West Initiative
Funded by Reclamation’s S&T Program
In collaboration with RNT Consulting

## Slide 6: Case Studies
Interviewed 13 hydropower plants with mussel infestations
  4 Reclamation (Hoover, Davis, Parker, Glen Canyon)
  3 Other agencies in USA (USACE, TVA, NY Power Authority)
  6 Canadian (Hydo Québec, Ontario Power Generation, Manitoba Hydro)

## Slide 7: Questions Asked
Design and operation
Mussel infestation timeline, response planning, and monitoring
Mussel impacts
  Systems/ components impacted
  Design aspects that prevented or reduced mussel impacts
  Unplanned or forced outages
Control methods utilized or examined
Expenses associated with mussels

## Slide 8: Plant Differences
  Design
  Use of raw water in the plant
  Different sizes
    2- 36 generator units (generating capacity 144-1899 MW)
  Mussel infestation timelines
    1-31 years

## Slide 9: Hoover Dam
Thrust bearing cooler plugging has resulted in unplanned outages
    1-3 outages per year
    3-5 days per outage
    8-12 people working on the outage
    $20,000 per day of lost production and unrealized revenue
    Estimated cost for 1 outage= $44,000- $80,000

## Slide 10: Hoover and Parker Dams
Hoover Dam
  Preventative control measures
    Conversion to tailbay water= $500,000
    Planned HOD UV installation= $2.1 million
Parker Dam
  Prior to UV, 8 weeks of labor per year to clean mussels and biofilm out of heat exchangers

## Slide 11: Glen Canyon Dam
Mussel settlement of the fixed wheel gates
  2 extra days to remove mussels
Maintenance changes
  Yearly to quarterly
  Quarterly to monthly
HOD UV installation planned

## Slide 12: Ontario Power Generation (4 plants)
First detected 1990
10-day chlorine treatment once per year
  Has controlled fouling in cooling system
  Capital investment $250,000- $1.3 million
  Yearly costs= $7,000- $24,000

## Slide 13: Wilson Hydropower Plant
Operated by TVA in Alabama
  21 generator units
  Mussels detected early 1990’s
  Chemical treatments not permitted
Mussel fouling most significant on units 1-8
  Service water source
    1-8 : Intake 14-ft below surface
    9-12: Bottom of penstock scroll case, 45-feet below surface

## Slide 14: Wilson Hydropower Plant
Cleaning the headers of units 1-8= $500,000 per cleaning
    Extensive outages required
    Cutting into pipes and hydro-blasting
Had 12 forced outages per year, now 3
    Optimized backwash flushing and temp/ flow monitoring
    Increased planned maintenance outages (10 per month)
Swap out generator air coolers when overheating occurs
    Purchased 4 replacement coolers= $72,000
    Requires outages, additional staff, and overtime= $4,000-$5,000 per swap

## Slide 15: Results
Impact
  Significant: 2 plants
  Moderate: 8 plants
  Little to none: 3 plants
Severity of impact
  Design and how raw water is used
  Not size or number of generators
  Mussel population cycles
5 of 13 plants had experienced unplanned outages
Mussel fouling expenses are not commonly recorded

## Slide 16: Control Approaches
Preventative treatments: 8 plants
  Chlorine $100,000- $1.3 million
  HOD UV $1 million- $2.1 million
Increased cleaning and operational changes: 5 plants

## Slide 17: Monitoring and Response Plans
7 of the 13 plants had a mussel facility vulnerability assessment or response plan
  Allowed control methods to be implemented before fouling became unmanageable
Most sites were not doing early detection monitoring
  Monitoring began after adults detected in the waterbody

## Slide 18
Hydropower Plant | Location | Waterbody | Waterbody Detection | Plant Detection or Issues | Years to Implement Controls
Hoover | USA, AZ/ NV | Colorado River, Lake Mead | 2007 | 2010 | 3
Davis and Parker | USA, AZ/ NV / CA | Colorado River, Lakes Mohave and Havasu | 2007 | 2008 | 1
Glen Canyon | USA, AZ/ UT | Colorado River, Lake Powell | 2012 | 2013 | 1
Beauharnois | Canada, Québec | St. Lawrence River, Lake St. Frances | 1990 | 1995 | 5
Jenpeg | Canada, Manitoba | Nelson River | 2013 | 2020 | 7
Lewiston | USA, NY | Niagara River | 1986 | 1990 | 4
Sir Adam Beck #1, Sir Adam Beck #2, DeCew NF23, Pump Generating Station | Canada, Ontario | Niagara River, Lake Gibson | 1988 | 1990-1998 | 2-10
Wilson | USA, Alabama | Tennessee River | Unknown | 1990 | ?
Gavins Point | USA, South Dakota | Missouri River, Lewis and Clark Lake | 2014 | 2016 | 2

## Slide 19: Recommendations
Risk assessment
Implement monitoring plan
Facility vulnerability assessment
Response plan

## Slide 20
Sherri Pucherelli
spucherelli@usbr.gov
303-445-2015